Copyright 2021 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

This Product MasterSpec Section is licensed by Deltek, Inc. to Rockfon (Rockwool International) ("Licensee").

This Product MasterSpec Section modifies the original MasterSpec text and does not include the full content of the original MasterSpec Section.

Revisions made to the original MasterSpec text are made solely by the Licensee and are not endorsed by, or representative of the opinions of, Deltek or The American Institute of Architects (AIA). Neither AIA nor Deltek are liable in any way for such revisions or for the use of this Product MasterSpec Section by any end user. A qualified design professional should review and edit the document to suit project requirements.

For more information, contact Rockfon (Rockwool International), 4849 S. Austin Ave., Chicago, IL 60638; Phone: (800) 323-7164; Fax: <Insert Fax number>; Website: www.rockfon.com/; Email: cs@rockfon.com.

For information about MasterSpec, contact Deltek at (800) 424-5080 or visit masterspec.com.

SECTION 095133 - ACOUSTICAL METAL PAN CEILINGS

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Access Product MasterSpec Sections:

<Double click here to view the list of manufacturer Sections available at ProductMasterSpec.com.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

MasterSpec includes provisions for LEED 2009, LEED v4, IgCC, and Green Globes.

- GENERAL

      - SUMMARY

        - Section Includes:

          - Acoustical metal pans and associated suspension system for interior ceilings.

        - Related Sections:

          - Section 095223 "Metal Acoustical Ceiling Suspension Assemblies."

          - Section 095400 "Specialty Ceilings."

          - Section 095800 "Integrated Ceiling Assemblies."

          - Section 134800 "Sound, Vibration, and Seismic Control."

          - Section 235000 "Central Heating Equipment."

          - Section 265000 "Lighting."

        - Related Requirements:

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

          - Section 095113 "Acoustical Panel Ceilings" for ceilings consisting of mineral-base and glass-fiber-base acoustical panels and exposed suspension systems.

          - Section 095123 "Acoustical Tile Ceilings" for ceilings consisting of mineral-base acoustical tiles used with concealed suspension systems, stapling, or adhesive bonding.

          - Section 095423 "Linear Metal Ceilings."

          - Section 095436 "Suspended Decorative Grids."

Retain paragraph below if cast-in-place attachment devices are required for Project.

        - Products furnished, but not installed, under this Section include anchors, clips, and other ceiling attachment devices to be cast in concrete.

      - REFERENCES

        - Abbreviations and Acronyms:

          - ASTM: American Society for Testing and Materials.

          - CISCA: Ceilings and Interior Systems Construction Association; www.cisca.org.

          - IBC: International Building Code.

          - ASCE 7-22 American Society of Civil Engineers, Minimum Design Loads for Buildings and Other Structures.

          - ICC-ES: International Code Council-Evaluation Service - AC 156 Acceptance Criteria for Seismic Qualification Testing of Non-structural Components.

          - ICC-ES: International Code Council-Evaluation Service Report - ESR 2631 Rockfon Chicago Metallic Corporation Suspended Ceiling Framing Systems and Suspension Ceiling Systems.

        - Reference Standards:

          - ASTM A1008/A1008M - Standard Specification for Steel, Sheet, Cold-Rolled, Carbon, Structural, High-Strength Low-Alloy, High-Strength Low-Alloy with Improved Formability, Required Harness, Solution Hardened, and Bake Hardenable

          - ASTM A641/A641M - Standard Specification for Zinc-Coated (Galvanized) Carbon Steel Wire

          - ASTM A653/A653M - Standard Specification for Steel Sheet, Zinc-Coated (Galvanized) or Zinc-Iron Alloy-Coated (Galvannealed) by the Hot-Dip Process

          - ASTM B209/B209M - Standard Specification for Aluminum and Aluminum-Alloy Sheet and Plate

          - ASTM C423 - Standard Test Method for Sound Absorption and Sound Absorption Coefficients by the Reverberation Room Method

          - ASTM C635/C635M - Standard Specification for Manufacture, Performance, and Testing of Metal Suspension Systems for Acoustical Tile and Lay-in Panel Ceilings

          - ASTM C636/C636M - Standard Practice for Installation of Metal Ceiling Suspension Systems for Acoustical Tile and Lay-In Panels

          - ASTM E84 	- Standard Test Method for Surface Burning Characteristics of Building Materials

          - ASTM E580/E580M - Standard Practice for Installation of Ceiling Suspension Systems for Acoustical Tile and Lay-in Panels in Areas Subject to Earthquake Ground Motions

          - ASTM E1111/E1111M - Standard Test Method for Measuring the Interzone Attenuation of Open Office Components

          - ASTM E1264 - Standard Classification for Acoustical Ceiling Products

          - ASTM E1414/E1414M - Standard Test Method for Airborne Sound Attenuation Between Rooms Sharing a Common Ceiling Plenum

          - UL 580 – Safety Testing for Uplift Resistance of Roof Assemblies

      - PREINSTALLATION MEETINGS

Retain "Preinstallation Conference" Paragraph below if Work of this Section is extensive or complex enough to justify a conference.

        - Preinstallation Conference: Conduct conference at [Project site] <Insert location>.

      - ACTION SUBMITTALS

Action submittals are submittals requiring responsive action and return of reviewed documents to Contractor.

        - Product Data: For each type of product. Include procedure for cutting metal pans.

Retain "Sustainable Design Submittals" Paragraph below if required to attain sustainability rating or to track sustainability submittals.

        - Sustainable Design Submittals:

Retain first "Product Data" Subparagraph below to require minimum recycled content for LEED 2009, MRc 4, "Recycled Content."

          - Product Data: For recycled content, indicating postconsumer and pre-consumer recycled content and cost.

"Product Data" Subparagraph below applies to LEED 2009 NC, CI, and CS; LEED v4; IgCC; ASHRAE 189.1; and Green Globes. Coordinate with requirements for adhesives and sealants.

Retain "Samples" Paragraph below for single-stage Samples, with a subordinate list if applicable. Retain "Samples for Initial Selection" and "Samples for Verification" paragraphs for two-stage Samples.

        - Samples: For each exposed product and for each color and texture specified, 6 inches (150 mm) in size.

        - Samples for Initial Selection: For units with factory-applied finishes.

        - Samples for Verification: For each component indicated and for each exposed finish required, prepared on Samples of size indicated below:

Delete first option in "Metal Pans" Subparagraph below if size of pans makes requirement impractical.

          - Metal Pans: Set of [full-size] [6-inch- (150-mm-) square] Samples of each type, finish, color, pattern, and texture. Show pan edge profile.

          - Exposed Suspension-System Members, Moldings, and Trim: Set of 6-inch- (150-mm-) long Samples of each type, finish, and color.

          - Sound Absorber: Sample of each type matching size of Sample metal pan.

Retain "Delegated Design Submittals" Paragraph below if design services have been delegated to Contractor.

        - Delegated Design Submittals: For design of [seismic restraints and ]attachment devices.

      - INFORMATIONAL SUBMITTALS

Informational submittals are submittals that require review by Architect, but they do not require Architect's responsive action and return of reviewed documents to Contractor, provided submittals comply with requirements. If rejected, submittals with responsive action must be returned to Contractor.

Retain "Coordination Drawings" Paragraph below for situations where limited space necessitates maximum utilization for efficient installation of different components or if coordination is required for installation of products and materials by separate installers. Coordinate paragraph with other Sections specifying products listed below. Preparation of coordination drawings requires the participation of each trade involved in installations within the limited space.

        - Coordination Drawings: Reflected ceiling plans, drawn to scale, on which the following items are shown and coordinated with each other, using input from installers of the items involved:

          - Suspended ceiling components.

          - Structural members to which suspension systems will be attached.

          - Size and location of access modules for acoustical panels.

          - Items penetrating finished ceiling including the following:

            - Lighting fixtures.

            - Air outlets and inlets.

            - Speakers.

            - Sprinklers.

            - Access panels.

            - <Insert item>.

          - Perimeter moldings.

Coordinate "Qualification Data" Paragraph below with qualification requirements in Section 014000 "Quality Requirements" and as may be supplemented in "Quality Assurance" Article.

        - Qualification Data: For testing agency.

        - Product Test Reports: For each acoustical metal pan ceiling, for tests performed by [manufacturer and witnessed by a qualified testing agency] [a qualified testing agency].

        - Evaluation Reports: For each acoustical metal pan ceiling suspension system[ and anchor and fastener type].

Retain "Field quality-control reports" Paragraph below if Contractor is responsible for field quality-control testing and inspecting.

        - Field quality-control reports.

      - CLOSEOUT SUBMITTALS

        - Maintenance Data: For finishes to include in maintenance manuals.

      - MAINTENANCE MATERIAL SUBMITTALS

        - Furnish extra materials that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

Revise "Acoustical Metal Pans( with Sound Absorber)," "Suspension-System Components," and "Hold-Down Clips" subparagraphs below to suit Project. If preferred, replace percentage option in each subparagraph with a specific number of metal pans and pieces of each suspension component and their lengths.

          - Acoustical Metal Pans[ with Sound Absorber]: Full-size units equal to [2] <Insert number> percent of quantity installed.

          - Suspension-System Components: Quantity of each grid, exposed molding, and trim equal to [2] <Insert number> percent of quantity installed.

          - Hold-Down Clips: [Equal to 2 percent of quantity installed] <Insert number>.

      - QUALITY ASSURANCE

Retain "Testing Agency Qualifications" Paragraph below if Contractor selects testing agency or if Contractor is required to provide services of a qualified testing agency in "Field Quality Control" Article. Qualification requirements are in addition to those specified in Section 014000 "Quality Requirements," which also defines "NRTL" (nationally recognized testing laboratory).

        - Testing Agency Qualifications: Qualified in accordance with NVLAP for testing indicated.

        - Mockups: Build mockups to verify selections made under Sample submittals, to demonstrate aesthetic effects, and to set quality standards for materials and execution.

Indicate portion of ceiling represented by mockup on Drawings or draw mockup as separate element.

          - Build mockup of typical ceiling area as indicated on Drawings.

Retain subparagraph below if the intention is to make an exception to the default requirement in Section 014000 "Quality Requirements" for demolishing and removing mockups.

          - Subject to compliance with requirements, approved mockups may become part of the completed Work if undisturbed at time of Substantial Completion.

      - DELIVERY, STORAGE, AND HANDLING

        - Deliver acoustical metal pans, suspension-system components, and accessories to Project site in original, unopened packages and store them in a fully enclosed, conditioned space where they are protected against damage from moisture, humidity, temperature extremes, direct sunlight, surface contamination, and other causes.

        - Handle acoustical metal pans, suspension-system components, and accessories carefully to avoid damaging units and finishes in any way.

- PRODUCTS

Manufacturers and products listed in this Section are neither recommended nor endorsed by the AIA or Deltek. Before selecting manufacturers and products, verify availability, suitability for intended applications, and compliance with minimum performance requirements. Product options commonly available from manufacturers are included in square brackets throughout the Section Text. Not every manufacturer listed can provide every option offered; verify availability with manufacturers. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

      - MANUFACTURERS

        - Metal Ceiling Systems: Rockfon, 4849 South Austin Avenue, Chicago, IL 60638. 1-800-323-7164; www.rockfon.com.

        - Suspension Systems: Rockfon, 4849 South Austin Avenue, Chicago, IL 60638. 1-800-323-7164; www.rockfon.com.

        - Aluminum Perimeter Trim: Rockfon, 4849 South Austin Avenue, Chicago, IL 60638. 1-800-323-7164; www.rockfon.com.

      - PERFORMANCE REQUIREMENTS

Retain "Delegated Design" Paragraph below if Contractor is required to assume responsibility for design.

        - Delegated Design: Engage a qualified professional engineer, as defined in Section 014000 "Quality Requirements," to design [seismic restraints and ]attachment devices.

        - Surface-Burning Characteristics: Comply with ASTM E84; testing by a qualified testing agency. Identify products with appropriate markings of applicable testing agency.

Retain one option in "Flame-Spread Index" Subparagraph below. Class A systems have a flame-spread index not exceeding 25 and a smoke-developed index not exceeding 50; Class B systems have a flame-spread index not exceeding 75 on face side; Class C systems have a flame-spread index not exceeding 200 on face side. Most products available in the United States are Class A.

          - Flame-Spread Index: Comply with ASTM E1264 for [Class A] [Class B] [Class C] materials.

          - Smoke-Developed Index: [50] [450] <Insert value> or less.

Unlike mineral composition units, acoustical metal pan units and ceilings are not tested in accordance with ASTM E119, are not listed in UL's "Fire Resistance Directory," and do not carry UL classification marking.

      - ACOUSTICAL METAL PANS, GENERAL

Retain "Source Limitations" Paragraph below if warranty requirements favor single-source ceiling systems or if ceiling units fit only same manufacturer's suspension system.

        - Source Limitations: Obtain each type of acoustical metal ceiling pan and supporting suspension system from single source from single manufacturer.

Retain "Recycled Content of Steel Products" Paragraph below to specify recycled content if required. An alternative method of requiring recycled content is to retain requirement in Project's Division 01 sustainable design requirements Section that gives Contractor the option and responsibility to determine how recycled content requirements will be met.

        - Recycled Content of Steel Products: Post-consumer recycled content plus one-half of pre-consumer recycled content not less than [25] <Insert number> percent.

Retain "Recycled Content of Aluminum Components" Paragraph below to specify recycled content if required. An alternative method of requiring recycled content is to retain requirement in Project's Division 01 sustainable design requirements Section that gives Contractor the option and responsibility to determine how recycled content requirements will be met.

        - Recycled Content of Aluminum Components: Post-consumer recycled content plus one-half of pre-consumer recycled content not less than [85] <Insert number> percent.

Retain "Recycled Content of Insulation" Paragraph below to specify recycled content if required. An alternative method of requiring recycled content is to retain requirement in Project's Division 01 sustainable design requirements Section that gives Contractor the option and responsibility to determine how recycled content requirements will be met.

        - Recycled Content of Insulation: Postconsumer recycled content plus one-half of pre-consumer recycled content not less than <Insert number> percent.

        - Acoustical Panel Standard: Provide manufacturer's standard pans of configuration indicated that comply with ASTM E1264 classifications as designated by types, patterns, acoustical ratings, and light reflectance unless otherwise indicated.

"Mounting Method for Measuring NRC" Subparagraph below represents standard mounting referenced in ASTM E1264. Revise if testing units with another mounting method is required for Project.

          - Mounting Method for Measuring NRC: Type E-400; plenum mounting in which face of test specimen is 15-3/4 inches (400 mm) away from test surface in accordance with ASTM E795.

      - LAY-IN AND TEGULAR PANS FOR ACOUSTICAL METAL PAN CEILING <Insert drawing designation>

If applicable, copy this article and re-edit for each product.

Insert drawing designation. Use same designation for both acoustical pans in this article and the suspension system that together make up the ceiling. Use these designations on Drawings to identify each product.

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

        - Basis-of-Design Product: Subject to compliance with requirements, provide Rockfon (Rockwool International); [PLANOSTILETM D Lay-in Metal Ceiling Panels] [PLANOSTILETM Lay-In Metal Ceiling Panels] or comparable product by one of the following:

          - American Decorative Ceilings (ADC).

          - CertainTeed Corporation.

          - USG Corporation.

          - <Insert manufacturer's name>.

        - Classification:

          - Aluminum Panels: Units complying with ASTM E1264 for [Type VII, perforated aluminum facing (pan) with mineral- or glass-fiber-base backing] [Type XX, other types described as perforated aluminum facing (pan) units with sound-absorbent fabric backing] [Type XX, other types described as unperforated aluminum facing (pan) units] <Insert Type XX description>.

          - Steel Panels: Units complying with ASTM E1264 for [Type V, perforated steel facing (pan) with mineral- or glass-fiber-base backing] [Type XX, other types described as perforated steel facing (pan) units with sound-absorbent fabric backing] [Type XX, other types described as unperforated steel facing (pan) units] <Insert Type XX description>.

          - Stainless Steel Panels: Units complying with ASTM E1264 for [Type XX, other types described as unperforated stainless steel facing (pan) units] <Insert Type XX description>.

          - Planostile Lay-in Perforations Available:

            - Aluminum and Steel Panels:

              - Perforations: Selected from manufacturer's full range.

              - Pattern: <Insert pattern designation for perforated pans and any requirements for perforation alignment, hole shape and size, holes per square foot or inch, percent open area, and border requirements>.

            - Stainless Steel Panels: Solid panels only.

          - Planostile D Lay-in Perforations Available: [E] [DD] [A].

        - Pan Fabrication: Manufacturer’s standard units of size, profile, and edge treatment indicated, formed from metal indicated and finished to comply with requirements indicated.

Retain "Lay-in Pans" Subparagraph below or insert description to suit Project. Coordinate pans with suspension system for a complete acoustical metal pan ceiling.

          - Lay-in Pans: Formed to set in exposed suspension grid.

          - <Insert type and description>.

        - Pan Thickness:

          - Planostile Lay-in Metal Panels:

            - Aluminum Panels: [0.032 inch (0.8 mm)] <Insert dimension>.

            - Steel and Stainless Steel Panels: [0.024 inch (0.61 mm)] <Insert dimension>.

          - Planostile D Lay-in Metal Panels: [0.040 inch (1.0 mm)] <Insert dimension>.

        - Pan Edge Detail:

          - Planostile Lay-in Metal Panels:

            - Aluminum and Steel Panels: [Square] [Flush Reveal] [9/16 inch Reveal] [15/16 inch Reveal] [Manufacturer's standard edge detail].

            - Stainless Steel Panels: Square.

Retain one or more options in first subparagraph below.

          - Planostile D Lay-in Metal Panels: [Upwards Reveal] [Downwards Reveal] [Sloped] [Diagonal] [Manufacturer's standard edge detail].

        - Pan Depth (for Planostile D Lay-in panels): [1 inch (25 mm)] [2 inch (50 mm)] [3 inch (76mm)] [4 inch (102 mm)].

        - Pan Size:

          - Planostile Lay-in Aluminum and Steel Square Edge and Reveal Edge Panels: [24 by 24 inches (610 by 610 mm)] [12 by 48 inches (305 by 1220 mm)] [24 by 48 inches (610 by 1220 mm)] [20 by 60 inches (508 by 1524 mm)] [24 by 60 inches (610 by 1524 mm)] [As indicated on Drawings] <Insert dimensions>.

          - [Planostile D Lay-in Panels] [Planostile Lay-in Flush Reveal Edge Panels] [Planostile Lay-in Stainless Steel Panels]: [24 by 24 inches (610 by 610 mm)] [As indicated on Drawings] <Insert dimensions>.

        - Pan Face Finish (as selected by Architect from Manufacturer's full range):

          - Planostile Lay-in Metal Panels:

            - Aluminum Panels: [Painted Finish] [Wood Grain Laminate] [Dye Sublimation Wood Grain Finish] [Aluminum Anodic Finish] [Metallic Reflective Finish] <Insert finish>.

            - Steel Panels: Painted Finish.

            - Stainless Steel Panels: 2B Finish.

          - Planostile D Lay-in Panels: Painted Finish.

Retain "NRC" Paragraph below if unperforated pans are not specified. Coordinate option retained with perforation pattern, sound absorber, and accessories selected.

        - NRC: Not less than [0.70] [0.90] <Insert number>.

        - Optional Acoustical Backing: Manufacturer's standard to provide NRC rating indicated for perforation pattern indicated.

          - Nonwoven Black Fabric, Factory Applied:

            - For perforated panels only.

            - Fabric layer, sized to fit concealed surface of pan, and consisting of black, nonwoven, nonflammable, sound-absorbent material.

            - Bond fabric layer to pan in the factory with manufacturer's standard nonflammable adhesive.

          - Black Poly-Wrapped Fiberglass Insulation Pad:

            - For perforated panels only.

            - Size: [24 by 24 inches (610 by 610 mm)] [24 by 48 inches (610 by 1220 mm)].

            - Thickness: [1 inch (25 mm)] [1-1/2 inch (38 mm)].

            - Density: 1 lb/cu. ft. (16 kg/cu. m).

      - SNAP-IN PANS FOR ACOUSTICAL METAL PAN CEILING <Insert drawing designation>

If applicable, copy this article and re-edit for each product.

Insert drawing designation. Use same designation for both acoustical pans in this article and the suspension system that together make up the ceiling. Use these designations on Drawings to identify each product.

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

        - Basis-of-Design Product: Subject to compliance with requirements, provide Rockfon (Rockwool International); PLANOSTILETM Snap-In Metal Ceiling Panels or comparable product by one of the following:

          - American Decorative Ceilings (ADC).

          - CertainTeed Corporation.

          - USG Corporation.

          - <Insert manufacturer's name>.

        - Classification:

          - Aluminum Panels: Units complying with ASTM E1264 for [Type VII, perforated aluminum facing (pan) with mineral- or glass-fiber-base backing] [Type XX, other types described as perforated aluminum facing (pan) units with sound-absorbent fabric backing] [Type XX, other types described as unperforated aluminum facing (pan) units] <Insert Type XX description>.

          - Steel Panels: Units complying with ASTM E1264 for [Type V, perforated steel facing (pan) with mineral- or glass-fiber-base backing] [Type XX, other types described as perforated steel facing (pan) units with sound-absorbent fabric backing] [Type XX, other types described as unperforated steel facing (pan) units] <Insert Type XX description>.

        - Planostile Snap-in Perforations Available:

          - Perforations: Selected from manufacturer's full range.

          - Pattern: <Insert pattern designation for perforated pans and any requirements for perforation alignment, hole shape and size, holes per square foot or inch, percent open area, and border requirements>.

        - Pan Fabrication: Manufacturer's standard units of size, profile, and edge treatment indicated, formed from metal indicated and finished to comply with requirements indicated.

Retain "Snap-in Pans" Subparagraph below or insert description to suit Project. Coordinate pans with suspension system for a complete acoustical metal pan ceiling.

          - Snap-in Pans: Designed with dimples or continuous beads on flanges for snap-in, secure engagement with concealed suspension system.

          - <Insert type and description>.

        - Pan Thickness:

          - Aluminum Pans: Not less than [0.032 inch (0.8 mm)] <Insert dimension>.

          - Steel Pans: Not less than [0.024 inch (0.61 mm)] <Insert dimension>.

        - Pan Edge Detail: [Square] [Beveled] [Manufacturer's standard edge detail].

Retain "Pan Joint Detail" Paragraph below if joint detail is not obvious for metal pan and suspension system selected.

        - Pan Size:

          - For Square Edge Panels: [24 by 24 inches (610 by 610 mm)] [12 by 48 inches (305 by 1220 mm)] [24 by 48 inches (610 by 1220 mm)] [20 by 60 inches (508 by 1524 mm)] [24 by 60 inches (610 by 1524 mm)] [As indicated on Drawings] <Insert dimensions>.

          - For Beveled Edge Panels: [24 by 24 inches (610 by 610 mm)] [As indicated on Drawings] <Insert dimensions>.

        - Pan Face Finish (as selected by Architect from Manufacturer's full range): [Painted Finish] [Wood Grain Laminate] [Dye Sublimation Wood Grain Finish] [Aluminum Anodic Finish] [Metallic Reflective Finish] <Insert finish>.

Retain "NRC" Paragraph below if unperforated pans are not specified. Coordinate option retained with perforation pattern, sound absorber, and accessories selected.

        - NRC: Not less than [0.70] [0.90] <Insert number>.

        - Optional Acoustical Backing: Manufacturer's standard to provide NRC rating indicated for perforation pattern indicated.

          - Nonwoven Black Fabric, Factory Applied:

            - For perforated panels only.

            - Fabric layer, sized to fit concealed surface of pan, and consisting of black, nonwoven, nonflammable, sound-absorbent material.

            - Bond fabric layer to pan in the factory with manufacturer's standard nonflammable adhesive.

          - Black Poly-Wrapped Fiberglass Insulation Pad:

            - For perforated panels only.

            - Size: [24 by 24 inches (610 by 610 mm)] [24 by 48 inches (610 by 1220 mm)].

            - Thickness: [1 inch (25-mm)] [1-1/2 inch (38-mm)].

            - Density: 1 lb/cu. ft. (16 kg/cu. m).

  - If applicable, copy this article and re-edit for each product.

Insert drawing designation. Use same designation for both acoustical pans in this article and the suspension system that together make up the ceiling. Use these designations on Drawings to identify each product.

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

      - Basis-of-Design Product: Subject to compliance with requirements, provide Rockfon (Rockwool International); [SPANAIRTM Torsion Spring Metal Ceiling Panels] [SPANAIRTM Torsion Spring Plus Metal Ceiling Panels] or comparable product by one of the following:

          - American Decorative Ceilings (ADC).

          - CertainTeed Corporation.

          - USG Corporation.

          - <Insert manufacturer's name>.

        - Classification: Units complying with ASTM E1264 for [Type VII, perforated aluminum facing (pan) with mineral- or glass-fiber-base backing] [Type XX, other types described as perforated aluminum facing (pan) units with sound-absorbent fabric backing] [Type XX, other types described as unperforated aluminum facing (pan) units] <Insert Type XX description>.

          - Perforations available for SPANAIRTM Torsion Spring Metal Ceiling Panels:

            - Perforations: Selected from manufacturer's full range.

            - Pattern: <Insert pattern designation for perforated pans and any requirements for perforation alignment, hole shape and size, holes per square foot or inch, percent open area, and border requirements>.

          - Perforations available for SPANAIRTM Torsion Spring Plus Metal Ceiling Panels:

            - Perforations: [Z] [AA].

        - Pan Fabrication: Manufacturer's standard units of size, profile, and edge treatment indicated, formed from metal indicated and finished to comply with requirements indicated.

Retain "Torsion-Spring-Hinged Pans" Subparagraph below or insert description to suit Project. Coordinate pans with suspension system for a complete acoustical metal pan ceiling.

          - Torsion-Spring-Hinged Pans: Designed to be securely retained in pre-slotted, exposed suspension grid by torsion springs provided by manufacturer.

          - <Insert type and description>.

        - Pan Thickness: Not less than [0.040 inch (1.0 mm)] <Insert dimension>.

        - Pan Edge Detail: Manufacturer's standard edge detail.

Retain "Pan Joint Detail" Paragraph below if joint detail is not obvious for metal pan and suspension system selected.

        - Pan Joint Detail: [Butt] <Insert description>.

        - Pan Size:

          - SPANAIRTM Torsion Spring Metal Ceiling Panels: [24 by 24 inches (610 by 610 mm)] [12 by 48 inches (305 by 1220 mm)] [24 by 48 inches (610 by 1220 mm)] [20 by 60 inches (508 by 1524 mm)] [24 by 60 inches (610 by 1524 mm)] [24 by 72 inches (610 by 1829 mm)] [24 by 96 inches (610 by 2439 mm)] [As indicated on Drawings] <Insert dimensions>.

          - SPANAIRTM Torsion Spring Plus Metal Ceiling Panels: [30 by 30 inches (762 by 762 mm)] [36 by 36 inches (915 by 915 mm)] [48 by 48 inches (1220 by 1220 mm)] [48 by 72 inches (1220 by 1829 mm)] [48 by 96 inches (1220 by 2439 mm)] [48 by 120 inches (1220 by 3048 mm)] [As indicated on Drawings] <Insert dimensions>.

        - Pan Face Finish (as selected by Architect from Manufacturer's full range):

          - SPANAIRTM Torsion Spring Metal Ceiling Panels: [Painted Finish] [Wood Grain Laminate] [Dye Sublimation Wood Grain Finish] [Aluminum Anodic Finish] [Metallic Reflective Finish] <Insert finish>.

          - SPANAIRTM Torsion Spring Plus Metal Ceiling Panels:  [Painted Finish] [Dye Sublimation Wood Grain Finish] <Insert finish>.

Retain "NRC" Paragraph below if unperforated pans are not specified. Coordinate option retained with perforation pattern, sound absorber, and accessories selected.

        - NRC: Not less than [0.70] [0.90] <Insert number>.

        - Optional Acoustical Backing: Manufacturer's standard to provide NRC rating indicated for perforation pattern indicated.

          - Nonwoven Black Fabric, Factory Applied:

            - For perforated panels only.

            - Fabric layer, sized to fit concealed surface of pan, and consisting of black, nonwoven, nonflammable, sound-absorbent material.

            - Bond fabric layer to pan in the factory with manufacturer's standard nonflammable adhesive.

          - Black Poly-Wrapped Fiberglass Insulation Pad:

            - For perforated panels only.

            - Size: [24 by 24 inches (610 by 610 mm)] [24 by 48 inches (610 by 1220 mm)].

            - Thickness: [1 inch (25 mm)] [1-1/2 inch (38 mm)].

            - Density: 1 lb/cu. ft. (16 kg/cu. m).

      - HOOK-ON ALUMINUM PANS FOR ACOUSTICAL METAL PAN CEILING <Insert drawing designation>

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

        - Basis-of-Design Product: Subject to compliance with requirements, provide Rockfon (Rockwool International); SPANAIRTM Hook-on Metal Ceiling Planks or comparable product by one of the following:

          - American Decorative Ceilings (ADC).

          - CertainTeed Corporation.

          - USG Corporation.

          - <Insert manufacturer's name>.

        - Classification: Units complying with ASTM E1264 for [Type VII, perforated aluminum facing (pan) with mineral- or glass-fiber-base backing] [Type XX, other types described as perforated aluminum facing (pan) units with sound-absorbent fabric backing] [Type XX, other types described as unperforated aluminum facing (pan) units] <Insert Type XX description>.

        - Perforations available for SPANAIRTM Hook-on Metal Ceiling Panels:

            - Perforations: Selected from manufacturer's full range.

            - Pattern: <Insert pattern designation for perforated pans and any requirements for perforation alignment, hole shape and size, holes per square foot or inch, percent open area, and border requirements>.

        - Pan Fabrication: Manufacturer's standard units of size, profile, and edge treatment indicated, formed from metal indicated and finished to comply with requirements indicated.

Retain "Hook-on Pans" Subparagraph below or insert description to suit Project. Coordinate pans with suspension system for a complete acoustical metal pan ceiling.

          - Hook-on Pans: Designated to be hooked on to special cross-tee with preinstalled J-Bar, factory-applied panel gaskets for stable concealed system.

          - <Insert type and description>.

        - Pan Thickness: Not less than [0.040 inch (1.0 mm)] <Insert dimension>.

        - Pan Edge Detail: Manufacturer's standard edge detail.

Retain "Pan Joint Detail" Paragraph below if joint detail is not obvious for metal pan and suspension system selected.

        - Pan Width: [9 inches (229 inches)] [12 inches (305 mm)] [24 inches (610 mm)] [As indicated on Drawings] <Insert dimensions>.

        - Pan Length: [48 inches (1220 mm)] [72 inches (1829 mm)] [96 inches (2439 mm)] [120 inches (3048 mm)] [As indicated on Drawings] <Insert dimensions>.

        - Pan Face Finish (as selected by Architect from Manufacturer's full range): [Painted Finish] [Wood Grain Laminate] [Dye Sublimation Wood Grain Finish] [Aluminum Anodic Finish] [Metallic Reflective Finish] <Insert finish>.

Retain "NRC" Paragraph below if unperforated pans are not specified. Coordinate option retained with perforation pattern, sound absorber, and accessories selected.

        - NRC: Not less than [0.70] [0.90] <Insert number>.

        - Optional Acoustical Backing: Manufacturer's standard to provide NRC rating indicated for perforation pattern indicated.

          - Nonwoven Black Fabric, Factory Applied:

            - For perforated panels only.

            - Fabric layer, sized to fit concealed surface of pan, and consisting of black, nonwoven, nonflammable, sound-absorbent material.

            - Bond fabric layer to pan in the factory with manufacturer's standard nonflammable adhesive.

          - Black Poly-Wrapped Fiberglass Insulation Pad:

            - For perforated panels only.

            - Size: [24 by 24 inches (610 by 610 mm)] [24 by 48 inches (610 by 1220 mm)].

            - Thickness: [1 inch (25 mm)] [1-1/2 inch (38 mm)].

      - HOOK-IN ALUMINUM PANS FOR ACOUSTICAL METAL PAN CEILING <Insert drawing designation>

If applicable, copy this article and re-edit for each product.

Insert drawing designation. Use same designation for both acoustical pans in this article and the suspension system that together make up the ceiling. Use these designations on Drawings to identify each product.

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

        - Basis-of-Design Product: Subject to compliance with requirements, provide Rockfon (Rockwool International); SPANAIRTM Hook-in Metal Ceiling Planks or comparable product by one of the following:

          - American Decorative Ceilings (ADC).

          - CertainTeed Corporation.

          - USG Corporation.

          - <Insert manufacturer's name>.

        - Classification: Units complying with ASTM E1264 for [Type VII, perforated aluminum facing (pan) with mineral- or glass-fiber-base backing] [Type XX, other types described as perforated aluminum facing (pan) units with sound-absorbent fabric backing] [Type XX, other types described as unperforated aluminum facing (pan) units] <Insert Type XX description>.

Retain "Pattern A," "Pattern B," or "Pattern" Subparagraph below for perforated pans. Coordinate pattern with acoustical performance and sound-absorbent assembly specified.

        - Perforations available for SPANAIRTM Hook-in Metal Ceiling Panels:

          - Perforations: Selected from manufacturer's full range.

          - Pattern: <Insert pattern designation for perforated pans and any requirements for perforation alignment, hole shape and size, holes per square foot or inch, percent open area, and border requirements>.

        - Pan Fabrication: Manufacturer's standard units of size, profile, and edge treatment indicated, formed from metal indicated and finished to comply with requirements indicated.

Retain "Hook-in Pans" Subparagraph below or insert description to suit Project. Coordinate pans with suspension system for a complete acoustical metal pan ceiling.

          - Hook-in Pans: Designated to be hooked in to main runner with specialized slotting to accept panel edges, factory applied panel gaskets for stable concealed system.

          - <Insert type and description>.

        - Pan Thickness: Not less than [0.040 inch (1.0 mm)] <Insert dimension>.

        - Pan Edge Detail: Manufacturer's standard edge detail.

Retain "Pan Joint Detail" Paragraph below if joint detail is not obvious for metal pan and suspension system selected.

        - Pan Width: [12 inches (305 mm)] [24 inches (610 mm)] [As indicated on Drawings] <Insert dimensions>.

        - Pan Length: [48 inches (1220 mm)] [60 inches (1524 mm)] [72 inches (1829 mm)] [96 inches (2439 mm)] [120 inches (3048 mm)] [As indicated on Drawings] <Insert dimensions>.

        - Pan Face Finish (as selected by Architect from Manufacturer's full range): [Painted Finish] [Wood Grain Laminate] [Dye Sublimation Wood Grain Finish] [Aluminum Anodic Finish] [Metallic Reflective Finish] <Insert finish>.

Retain "NRC" Paragraph below if unperforated pans are not specified. Coordinate option retained with perforation pattern, sound absorber, and accessories selected.

        - NRC: Not less than [0.70] [0.90] <Insert number>.

        - Optional Acoustical Backing: Manufacturer's standard to provide NRC rating indicated for perforation pattern indicated.

          - Nonwoven Black Fabric, Factory Applied.

            - For perforated panels only.

            - Fabric layer, sized to fit concealed surface of pan, and consisting of black, nonwoven, nonflammable, sound-absorbent material.

            - Bond fabric layer to pan in the factory with manufacturer's standard nonflammable adhesive.

          - Black Poly-Wrapped Fiberglass Insulation Pad:

            - For perforated panels only.

            - Size: [24 by 24 inches (610 by 610 mm)] [24 by 48 inches (610 by 1220 mm)].

            - Thickness: [1 inch (25 mm)] [1-1/2 inch (38 mm)].

            - Density: 1 lb/cu. ft. (16 kg/cu. m).

      - CLIP-IN ALUMINUM PANS FOR ACOUSTICAL METAL PAN CEILING <Insert drawing designation>

If applicable, copy this article and re-edit for each product.

Insert drawing designation. Use same designation for both acoustical pans in this article and the suspension system that together make up the ceiling. Use these designations on Drawings to identify each product.

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

        - Basis-of-Design Product: Subject to compliance with requirements, provide Rockfon (Rockwool International); SPANAIRTM Clip-In Metal Ceiling Panels or comparable product by one of the following:

          - American Decorative Ceilings (ADC).

          - CertainTeed Corporation.

          - USG Corporation.

          - <Insert manufacturer's name>.

        - Classification: Units complying with ASTM E1264 for [Type VII, perforated aluminum facing (pan) with mineral- or glass-fiber-base backing] [Type XX, other types described as perforated aluminum facing (pan) units with sound-absorbent fabric backing] [Type XX, other types described as unperforated aluminum facing (pan) units] <Insert Type XX description>.

Retain "Pattern A," "Pattern B," or "Pattern" Subparagraph below for perforated pans. Coordinate pattern with acoustical performance and sound-absorbent assembly specified.

        - Perforations available for SPANAIRTM Clip-in Metal Ceiling Panels:

          - Perforations: Selected from manufacturer's full range.

          - Pattern: <Insert pattern designation for perforated pans and any requirements for perforation alignment, hole shape and size, holes per square foot or inch, percent open area, and border requirements>.

        - Pan Fabrication: Manufacturer's standard units of size, profile, and edge treatment indicated, formed from metal indicated and finished to comply with requirements indicated.

Retain "Clip-in Pans" Subparagraph below or insert description to suit Project. Coordinate pans with suspension system for a complete acoustical metal pan ceiling.

          - Clip-in Pans: Designed to clip in and be securely retained in exposed suspension grid by formed edges or accessory clips provided by manufacturer.

          - <Insert type and description>.

        - Pan Thickness: Not less than [0.032 inch (0.8 mm)] <Insert dimension>.

        - Pan Edge Detail: [Concealed] [Semi-Concealed] [Manufacturer's standard edge detail].

Retain "Pan Joint Detail" Paragraph below if joint detail is not obvious for metal pan and suspension system selected.

        - Pan Size: [24 by 24 inches (610 by 610 mm)] [12 by 48 inches (305 by 1220 mm)] [24 by 48 inches (610 by 1220 mm)] <Insert dimensions>.

        - Pan Face Finish (as selected by Architect from Manufacturer's full range): [Painted Finish] [Wood Grain Laminate] [Dye Sublimation Wood Grain Finish] [Aluminum Anodic Finish] [Metallic Reflective Finish] <Insert finish>.

Retain "NRC" Paragraph below if unperforated pans are not specified. Coordinate option retained with perforation pattern, sound absorber, and accessories selected.

        - NRC: Not less than [0.70] [0.90] <Insert number>.

        - Optional Acoustical Backing: Manufacturer's standard to provide NRC rating indicated for perforation pattern indicated:

          - Nonwoven Black Fabric, Factory Applied:

            - For perforated panels only.

            - Fabric layer, sized to fit concealed surface of pan, and consisting of black, nonwoven, nonflammable, sound-absorbent material.

            - Bond fabric layer to pan in the factory with manufacturer’s standard nonflammable adhesive.

          - Black Poly-Wrapped Fiberglass Insulation Pad:

            - For perforated panels only.

            - Size: [24 by 24 inches (610 by 610 mm)] [24 by 48 inches (610 by 1220 mm)].

            - Thickness: [1 inch (25 mm)] [1-1/2 inch (38 mm)].

            - Density: 1 lb/cu. ft. (16 kg/cu. m).

If applicable, copy this article and re-edit for each product.

Insert drawing designation. Use same designation for both acoustical pans in this article and the suspension system that together make up the ceiling. Use these designations on Drawings to identify each product.

Retain “Basis-of-Design Product” Paragraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

      - METAL SUSPENSION SYSTEM FOR STANDARD-GRID METAL PAN CLIP-IN, LAY-IN AND TEGULAR CEILING <Insert drawing designation>

        - Suspension System: For [lay-in/tegular] [clip-in] <Insert type> pans.

        - Metal Suspension-System Standard: Provide manufacturer's standard, direct-hung, metal suspension system and accessories in accordance with ASTM C635/C635M and designated by type, structural classification, and finish indicated.

Retain "High-Humidity Finish" Subparagraph below if required. Indicate on Drawings where high-humidity finish is required.

          - High-Humidity Finish: Where indicated, provide coating tested and classified for "severe environment performance" in accordance with ASTM C635/C635M.

Retain "Recycled Content" Paragraph below to specify recycled content if required. An alternative method of requiring recycled content is to retain requirement in Project's Division 01 sustainable design requirements Section that gives Contractor the option and responsibility to determine how recycled content requirements will be met.

        - Recycled Content: Postconsumer recycled content plus one-half of pre-consumer recycled content not less than [25] <Insert number> percent.

Retain one of four suspension-system paragraphs below. Paragraphs are examples of suspension systems for acoustical panel ceilings; revise to suit Project.

Before retaining options in remaining subparagraphs, verify availability with manufacturers. Coordinate edge and joint details of acoustical panels with main- and cross-runner configurations of suspension systems under consideration, to ensure compatibility between panels and system members.

Retain option in "Wide-Face, Capped, Double-Web, Steel Suspension System" Paragraph below along with permitted fire-resistance-rated acoustical panel if fire-rated assembly is required; revise to suit Project.

        - Wide-Face, Capped, Double-Web, Steel Suspension System: Main and cross runners roll formed from cold-rolled steel sheet; prepainted, electrolytically zinc coated, or hot-dip galvanized, [G30 (Z90)] [G90 (Z275)] coating designation; with prefinished 15/16-inch- (24-mm-) wide metal caps on flanges.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Chicago Metallic by Rockfon; [1200 (Stab) Seismic 15/16 inch (24 mm)] [200 Snap-Grid (Hook) 15/16 inch (24 mm)] or comparable product by one of the following:

            - Armstrong Ceilings & Wall Solutions.

            - CertainTeed Corporation.

            - USG Corporation.

            - <Insert manufacturer’s name>.

          - Suspension System: For [clip-in] [lay-in/tegular] <Insert type> pans.

          - Structural Classification: [Intermediate] [Heavy]-duty system.

          - End Condition of Cross Runners: [Override (stepped)] [or] [butt-edge] type.

          - Face Design: Flat, flush.

          - Cap Material: [Cold-rolled steel] [or] [aluminum].

Coordinate finish in "Cap Finish" Subparagraph below with cap material selected.

          - Cap Finish: [Painted white] [Painted black] [Painted satin silver] [Painted in color as selected from manufacturer’s full range] [Painted to match existing color] [Painted custom color].

        - Narrow-Face, Capped, Double-Web, Steel Suspension System: Main and cross runners roll formed from cold-rolled steel sheet; prepainted, electrolytically zinc coated, or hot-dip galvanized, G30 (Z90) coating designation; with prefinished 9/16-inch- (15-mm-) wide metal caps on flanges.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Chicago Metallic by Rockfon; 4000 Tempra 9/16 inch (15 mm) or comparable product by one of the following:

            - Armstrong Ceilings & Wall Solutions.

            - CertainTeed Corporation.

            - USG Corporation.

            - <Insert manufacturer's name>.

          - Suspension System: For [lay-in/tegular] <Insert type> pans.

          - Structural Classification: [Intermediate] [Heavy]-duty system.

          - End Condition of Cross Runners: [Override (stepped)] [or] [butt-edge] type.

          - Face Design: [Flat, flush] [Flanges formed with an integral center reveal].

          - Cap Material: [Cold-rolled steel] [or] [aluminum].

Coordinate finish in "Cap Finish" Subparagraph below with cap material selected.

          - Cap Finish: [Painted white] [Painted black] [Painted satin silver] [Painted in color as selected from manufacturer's full range] [Painted to match existing color] [Painted custom color].

        - Narrow-Face, Uncapped, Double-Web, [Fire-Rated, ]Steel Suspension System: Main and cross runners roll formed from cold-rolled steel sheet; prepainted, electrolytically zinc coated, or hot-dip galvanized, G30 (Z90) coating designation; to produce structural members with 9/16-inch- (15-mm-) wide faces.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Chicago Metallic by Rockfon; [4200 Integrity 9/16-inch (15-mm)] [4600 Ultraline (Stab) 9/16-inch (15-mm) Bolt-Slot 1/8-inch (3.2-mm) Reveal] [4500 Ultraline (Stab) 9/16-inch (15-mm) Bolt-Slot 1/4-inch (6.35-mm) Reveal] [4550 Ultraline Fire Rated (Stab) 9/16-inch (15-mm) Bolt-Slot 1/4-inch (6.35-mm) Reveal] or comparable product by one of the following:

            - <Insert manufacturer's name>.

            - <Insert manufacturer's name>.

            - <Insert manufacturer's name>.

          - Structural Classification: [Intermediate] [Heavy]-duty system.

          - Face Finish: Painted [white] [in color as selected from manufacturer's full range] [to match color indicated by manufacturer's designation] [to match color of acoustical unit].

          - Reveal Finish: Painted [to match flange color] [white] [black].

Retain "Narrow-Face, Steel-Capped, Double-Web, Fire-Rated Steel Suspension System" Paragraph below along with permitted fire-resistance-rated acoustical panel if fire-rated assembly is required for Project.

        - Wide-Face, Aluminum-Capped, Double-Web, Hot-Dip Galvanized, G60 (Z180), Steel Suspension System: Main and cross runners roll formed from cold-rolled steel sheet; hot-dip galvanized, G60 (Z180) coating designation; with prefinished, 15/16-inch- (24-mm-) wide aluminum caps on flanges.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Chicago Metallic by Rockfon; [1260/1280 Seismic 15/16 inch (24 mm) with Aluminum Cap] or comparable product by one of the following:

            - Armstrong Ceilings & Wall Solutions.

            - CertainTeed Corporation.

            - USG Corporation.

            - <Insert manufacturer's name>.

          - Suspension System: For [lay-in/tegular] <Insert type> pans.

          - Structural Classification: [Intermediate] [Heavy]-duty system.

          - Face Design: Flat, flush.

          - Cap Finish: [Painted white] [Painted to match color indicated by manufacturer's designation] [Painted to match color of acoustical unit] [Natural finish].

        - Wide-Face, Single-Web, Steel Suspension System: Main and cross runners roll formed from cold-rolled steel sheet electrolytically zinc coated[ and aluminum capped], with prefinished flanges of width indicated.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Chicago Metallic by Rockfon; [660 Wide Face (Stab) 1-3/8 in (34.9 mm)] (or comparable product by one of the following:

            - Armstrong Ceilings & Wall Solutions.

            - CertainTeed Corporation.

            - USG Corporation.

            - <Insert manufacturer's name>.

          - Suspension System: For [lay-in/tegular] <Insert type> pans

          - Structural Classification: Heavy-duty system.

          - Face Finish: Painted [white] [black].

      - METAL SUSPENSION SYSTEM FOR STANDARD SNAP-IN METAL CEILING <Insert drawing designation>

        - Snap-bar main runners formed to receive the vertical flanges of snap-in panels with tight panel interlock, alignment and adjacent panels level at the ceiling plane. Formed from 0.020 in. HDG steel.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Chicago Metallic by Rockfon; Planostile Snap-in Concealed Snap-Bar Carrier or comparable product by one of the following:

            - Armstrong Ceilings & Wall Solutions.

            - CertainTeed Corporation.

            - USG Corporation.

            - <Insert manufacturer's name>.

      - METAL SUSPENSION SYSTEM FOR STANDARD TORSION SPRING METAL CEILING <Insert drawing designation>

        - T-shape main runner with knurled face. Formed with slots in grid face to properly receive the torsion springs of the panels and to ensure panel locking and alignment. The main carrier shall be formed from .020 hot dipped galvanized steel.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Chicago Metallic by Rockfon; Spanair Torsion Spring Concealed Slotted Carriers or comparable product by one of the following:

            - Armstrong Ceilings & Wall Solutions.

            - CertainTeed Corporation.

            - USG Corporation.

            - <Insert manufacturer's name>.

      - METAL SUSPENSION SYSTEM FOR STANDARD HOOK-ON METAL CEILING <Insert drawing designation>

        - T-shape main runner with 1-3/8 inch knurled face. The main carrier shall be formed from .020 hot dipped galvanized steel.

        - T-shaped cross tee with knurled face formed from .020 hot dopped galvanized steel. J-shape bar manufactured of 0.040 galvanized steel is factory mechanically fastened to the cross tee web to receive hook-on ends of planks.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Chicago Metallic by Rockfon; Spanair Hook-on Concealed Slotted Carriers or comparable product by one of the following:

            - Armstrong Ceilings & Wall Solutions.

            - CertainTeed Corporation.

            - USG Corporation.

            - <Insert manufacturer's name>.

      - METAL SUSPENSION SYSTEM FOR STANDARD HOOK-IN METAL CEILING <Insert drawing designation>

        - T-shape main runner with 1-3/8 inch knurled face. The main carrier shall be formed from .020 hot dipped galvanized steel.

        - Formed with openings in grid web to receive tabs of hook-in panels.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Chicago Metallic by Rockfon; Spanair Hook-in Concealed Slotted Carriers or comparable product by one of the following:

            - Armstrong Ceilings & Wall Solutions.

            - CertainTeed Corporation.

            - USG Corporation.

            - <Insert manufacturer's name>.

      - SPECIALTY PERIMETER MOLDINGS AND TRIM <Insert drawing designation>

Delete this article if only snap-in metal pan ceilings are required.

Copy this article and re-edit for each product.

Insert drawing designation. Use same designation for both the suspension system in this article and the acoustical metal pans that together make up the ceiling. Use these designations on Drawings to identify each product.

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

        - Basis-of-Design Product: Subject to compliance with requirements, provide Rockfon; Infinity or comparable product by one of the following:

          - CertainTeed Corporation.

          - Fry Reglet Corporation.

          - Gordon, Inc.

          - USG Corporation.

          - <Insert manufacturer's name>.

        - Panels: Manufactured from extruded 6063-T5 aluminum, complete with continuous integral slots for attachment of splice plates and grid clips.

        - Profile:

          - "Rockfon Infinity" profile perimeter trim for T-bar type grid acoustical and lay-in, snap-in, torsion spring, hook-in, hook-on and clip-in metal ceilings [2 inches (50 mm)] [4 inches (100 mm)] [6 inches (150 mm)] [8 inches (200 mm)] [10 inches (250 mm)] [12 inches (300 mm)] high with horizontal face. [Straight] [and] [curved] panels as indicated on approved Drawings. [Each corner to be factory mitered.] [90-degree corner kits are allowed in place of mitered corners on straight sections.] Factory apply paint finish [on outside surface] [360 degrees]; [Painted Finish]  [Dye Sublimation Wood Grain Finish] <Insert finish>.

          - "Rockfon Infinity R Reveal" profile perimeter trim for T-bar type grid acoustical ceilings and lay-in, snap-in, torsion spring, hook-in, hook-on and clip-in metal ceilings [4-inch (100-mm-)] high by 3/4-inch- (19-mm-) horizontal face, and 1/2-inch- (12.7-mm-) wide by 3/4-inch- (19-mm-) deep continuous open reveal. Straight panels as indicated on approved Drawings. Each corner to be factory mitered. Factory apply paint finish [on outside surface] [360 degrees]; [on outside surface] [360 degrees]; [Painted Finish]  [Dye Sublimation Wood Grain Finish] <Insert finish>.

          - "Rockfon Infinity Z Razor" profile for T-bar-type grid acoustical ceilings and lay-in, snap-in, torsion spring, hook-in, hook-on and clip-in metal ceilings, 6-inch- (150-mm-) wide horizontal face by 1-5/8 inches (41 mm) high. Straight panels as indicated on approved Drawings. Each corner to be factory mitered a maximum 45 degrees. Factory apply paint finish [on outside surface] [360 degrees]; [Painted Finish] [Dye Sublimation Wood Grain Finish] <Insert finish>.

          - "Rockfon Infinity CDX Concealed" profile for T-bar-type grid acoustical ceilings, 6-inch (150-mm) high by 3/4-inch (19-mm) horizontal face, elevated to allow easy integration of concealed and semi-concealed edge acoustical ceilings. Each corner to be factory mitered. Factory apply paint finish. [on outside surface] [360 degrees]; [Painted Finish] [Dye Sublimation Wood Grain Finish] <Insert finish>.

          - "Rockfon Infinity CDX/SCD Razor" profile for T-bar-type grid acoustical ceilings and, 6-inch- (150-mm-) wide horizontal face by 2-7/16 inches (62 mm) high. Horizontal face elevated to accept concealed and semi-concealed edge acoustical ceilings. Straight panels as indicated on approved Drawings. Each corner to be factory mitered a maximum 45 degrees. Factory apply paint finish on outside surface; [on outside surface] [360 degrees]; [Painted Finish] [Dye Sublimation Wood Grain Finish] <Insert finish>.

        - Splice Plate: Manufactured from galvanized steel with set screw for splicing sections of perimeter trim.

        - Grid Clips: Manufactured from galvanized steel with set screw for attaching perimeter trim to suspension system members.

- EXECUTION

      - EXAMINATION

        - Examine substrates, areas, and conditions, including structural framing to which acoustical metal pan ceilings attach or abut, with Installer present, for compliance with requirements specified in this and other Sections that affect ceiling installation and anchorage and with requirements for installation tolerances and other conditions affecting performance of acoustical metal pan ceilings.

        - Prepare written report, endorsed by Installer, listing conditions detrimental to performance of the Work.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - PREPARATION

        - Measure each ceiling area and establish layout of acoustical metal pans to balance border widths at opposite edges of each ceiling. Avoid using less-than-half-width pans at borders, and comply with layout shown on reflected ceiling plans and coordination drawings.

      - INSTALLATION

        - General: Install acoustical metal pan ceiling assemblies to comply with ASTM C636/C636M[, seismic design requirements,] and manufacturer's written instructions.

        - Suspend ceiling hangers from building's structural members and as follows:

          - Install hangers plumb and free from contact with insulation or other objects within ceiling plenum that are not part of supporting structure or of ceiling suspension system.

          - Splay hangers only where required[ and, if permitted with fire-resistance-rated ceilings,] to miss obstructions; offset resulting horizontal forces by bracing, countersplaying, or other equally effective means.

          - Where width of ducts and other construction within ceiling plenum produces hanger spacings that interfere with location of hangers at spacings required to support standard suspension-system members, install supplemental suspension members and hangers in form of trapezes or equivalent devices.

Retain first subparagraph below if applicable and indicate hanger locations by inserting below or indicating on Drawings. Retain option below if using indirect-hung snap-in metal pan ceilings.

          - Secure wire hangers to ceiling suspension members[ or carrying channels] and to supports above with a minimum of three tight turns. Connect hangers directly either to structures or to inserts, eye screws, or other devices that are secure and appropriate for substrate and that do not deteriorate or otherwise fail due to age, corrosion, or elevated temperatures.

Retain first subparagraph below if applicable and indicate hanger locations by inserting below or indicating on Drawings. Retain option below if using indirect-hung snap-in metal pan ceilings.

          - Secure flat, angle, channel, and rod hangers to ceiling suspension members[ or carrying channels] and to structure, including intermediate framing members, by attaching to inserts, eye screws, or other devices that are secure and appropriate for both structure to which hangers are attached and the type of hanger involved. Install hangers in a manner that does not cause them to deteriorate or fail due to age, corrosion, or elevated temperatures.

Retain one or more of six subparagraphs below that refer to applicable construction types.

Revise first subparagraph below if power-actuated fasteners are not allowed. Also, revise if attaching to permanent metal forms or the floor deck is permitted by the structural engineer and authorities having jurisdiction.

          - Do not support ceilings directly from permanent metal forms or floor deck. Fasten hangers to cast-in-place hanger inserts, postinstalled mechanical or adhesive anchors, or power-actuated fasteners that extend through forms into concrete.

          - When steel framing does not permit installation of hanger wires at spacing required, install carrying channels or other supplemental support for attachment of hanger wires.

          - Do not attach hangers to steel deck tabs.

Retain first subparagraph below unless attaching to the roof deck is permitted by the structural engineer and authorities having jurisdiction. Revise if structural members are spaced too far apart for hangers and another method is required. For alternatives that may need to be detailed on Drawings, consult Project's structural engineer.

          - Do not attach hangers to steel roof deck. Attach hangers to structural members.

          - Space hangers not more than 48 inches (1200 mm) o.c. along each member supported directly from hangers unless otherwise indicated; provide hangers not more than 8 inches (200 mm) from ends of each member.

          - Size supplemental suspension members and hangers to support ceiling loads within performance limits established by referenced standards and publications.

First paragraph below is based on requirements of the Division of the State Architect in California, for ceilings in hospitals and schools. ASTM C636/C636M requires three full turns (360 degrees each) within a 3-inch (75-mm) length. Revise or delete if not required. Retain option below if using indirect-hung snap-in metal pan ceilings.

        - Secure bracing wires to ceiling suspension members[ or carrying channels] and to supports with a minimum of four tight turns. Suspend bracing from building's structural members as required for hangers, without attaching to permanent metal forms, steel deck, or steel deck tabs. Fasten bracing wires into concrete with cast-in-place or postinstalled anchors.

        - Install edge moldings and trim of type indicated at perimeter of acoustical ceiling area and where necessary to conceal edges of acoustical metal pans.

Retain subparagraphs below to eliminate air movement and light and sound leaks at edges of ceiling.

          - Apply acoustical sealant in a continuous ribbon concealed on back of vertical legs of moldings before they are installed.

          - Screw attach moldings to substrate at intervals not more than 16 inches (400 mm) o.c. and not more than 3 inches (75 mm) from ends, leveling with ceiling suspension system to a tolerance of 1/8 inch in 12 ft. (3.2 mm in 3.6 m). Miter corners accurately and connect securely.

Delete subparagraph below or revise if exposed fasteners are allowed.

          - Do not use exposed fasteners, including pop rivets, on moldings and trim.

        - Install suspension-system runners so they are square and securely interlocked with one another. Remove and replace dented, bent, or kinked members.

Revise first paragraph below and insert requirements in Part 2 if penetrations for light fixtures, sprinklers, and similar fixtures are factory cut. Verify availability with manufacturers.

        - Cut acoustical metal pan units for accurate fit at borders and at interruptions and penetrations by other work through ceilings. Stiffen edges of cut units as required to eliminate evidence of buckling or variations in flatness exceeding referenced standards for stretcher-leveled metal sheet. Cut and treat edges to comply with manufacturer's written instructions.

        - Install acoustical metal pans in coordination with suspension system and exposed moldings and trim. Comply with manufacturer's installation tolerances.

Retain applicable subparagraphs below that coordinate with metal-pan type, pan edge and joint details, and suspension-system types, or revise to suit Project.

Retain one of first three subparagraphs below for lay-in pans, or insert another.

          - For lay-in, square-edge pans, install pans with edges fully hidden from view by flanges of suspension-system runners and moldings.

          - For lay-in, reveal-edge pans on suspension-system runners, install pans with bottom of reveal in firm contact with top surface of runner flanges.

          - For lay-in, reveal-edge pans on suspension-system members with box-shaped flanges, install pans with reveal surfaces in firm contact with suspension-system surfaces and panel faces flush with bottom face of runners.

          - For [clip-in] [torsion-spring-hinged] pans, position pans in accordance with manufacturer's written instructions.

          - For snap-in pans, fit adjoining units to form flush, tight joints.

          - Align joints in adjacent courses to form uniform, straight joints parallel to room axis in both directions unless otherwise indicated.

          - Fit adjoining units to form flush, tight joints.

Retain first subparagraph below if applicable. Indicate locations of directionally patterned or textured pans on Drawings, or insert locations here.

          - Install directionally patterned or textured metal pans in directions indicated.

Usually, delete both subparagraphs below if only unperforated patterns are specified. Delete first subparagraph if acoustical fabric is bonded to pan in factory.

          - Install sound-absorbent fabric layers in, and bond to, perforated metal pans.

          - Install sound-absorbent pads in perforated metal pans[ over metal spacer grids].

        - Install sound attenuation panels in areas indicated by reflected ceiling plans or room finish schedules. Lay panels directly on ceiling system and close major openings to form complete coverage in required areas. Lay second sound-absorbent pads on sound attenuation panels.

        - Install hold-down clips where indicated.

      - FIELD QUALITY CONTROL

Retain this article if applicable. ASCE/SEI 7 requires special inspections for suspended ceiling systems in Seismic Design Categories D, E, and F; verify requirements of applicable building code.

Retain first option in "Special Inspections" Paragraph below if Owner engages special inspector. Consider retaining second option if authorities having jurisdiction allow Contractor to engage special inspector. If retaining second option, retain "Field quality-control reports" Paragraph in "Informational Submittals" Article.

        - Special Inspections: [Owner will engage] [Engage] a qualified special inspector to perform the following special inspections:

          - Seismic design compliance.

Retain "Testing Agency" Paragraph below, with or without "Special Inspections" Paragraph above, to identify who performs tests and inspections. If retaining second option in "Testing Agency" Paragraph, retain "Field quality-control reports" Paragraph in "Informational Submittals" Article.

        - Testing Agency: [Owner will engage] [Engage] a qualified testing agency to perform tests and inspections.

Retain "Perform the following test and inspections" Paragraph below to require Contractor to perform tests and inspections. Testing requirements are examples only and apply only to ceilings with hangers attached to concrete by power-actuated fasteners and postinstalled anchors.

        - Perform the following tests and inspections of completed installations of acoustical metal panel ceiling hangers, anchors, and fasteners in successive stages. Do not proceed with installations of acoustical metal panel ceiling hangers for the next area until test results for previously completed installations show compliance with requirements.

          - Extent of Each Test Area: When installation of ceiling suspension systems on each floor has reached 20 percent completion, but no panels have been installed.

Verify loadings in two subparagraphs below with structural engineer based on ceiling loadings and seismic zone where Project is located. CISCA's "Guidelines for Seismic Restraint of Direct-Hung Suspended Ceiling Assemblies - Seismic Zones 3 & 4" requires hanger wire attachment devices to be "capable of supporting 100 lbf (445 N)."

            - Within each test area, testing agency selects one of every 10 power-actuated fasteners and postinstalled anchors used to attach hangers to concrete and tests them for 200 lbf (890 N) of tension; it also selects one of every two postinstalled anchors used to attach bracing wires to concrete and tests them for 440 lbf (1957 N) of tension.

            - When tested fasteners and anchors do not comply with requirements, testing agency tests those fasteners and anchors not previously tested until 20 pass consecutively and then resumes initial testing frequency.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

        - Acoustical metal panel ceiling hangers, anchors, and fasteners will be considered defective if they do not pass tests and inspections.

        - Prepare test and inspection reports.

Insert other field quality-control procedures required for Project.

      - CLEANING

        - Clean exposed surfaces of acoustical metal pan ceilings, including trim and edge moldings, after removing strippable, temporary protective covering, if any. Comply with manufacturer's written instructions for stripping of temporary protective covering, cleaning, and touchup of minor finish damage. Remove and replace ceiling components that cannot be successfully cleaned and repaired to permanently eliminate evidence of damage, including dented and bent units.

END OF SECTION 095133